## Sheet1
Online High Frequency UPS (1/1 phase)
Parameter
Model |  | VT1KVA | VT1KS | VT2KVA | VT2KS | VT3KVA | VT3KS
Rated Power |  | 1kVA/0.9kW |  | 2kVA/1.8kW |  | 3kVA/2.7kW
Input | Voltage Range | 90-285Vac 1P2W+G
| Working Frequency Range | 40-70Hz (settable)
| Input Power Factor | ≥0.99
Output | Rated Voltage and Accuracy | 220Vac(1±2%) 1P2W+G
| Output Frequency | 50Hz
| Rated Current | 4.5A |  | 9.1A |  | 13.6A
| Output Power Factor | 0.9
| Output Harmonic Wave | ≤4% (Full R load)
| Crest Factor |  |  | 3:01
| Output Overload | Overload pre-warning :100%±2%＜Load Output warning:102%±2%≤Load≤110%±2%: Convert to bypass mode and alarm after 30mins;
Output warning:110%±2%＜Load≤130%±2%: Convert to bypass mode and alarm after 10mins;
Output warning:130%±2%＜Load≤150%±2%: Convert to bypass mode and alarm after 30s; Convert to bypass mode and alarm after 200ms, Load＞150%±2%
Conversion time between Mains Power and Battery |  | 0ms
Efficiency |  | ≥90% (Normal mode)
Battery | Rated Voltage | 24Vdc | 36Vdc | 48Vdc | 72Vdc | 72Vdc | 96Vdc
| Quantity | 2 | External | 4 | External | 6 | External
| Charging Current | 1A | 5.5A | 1A | 5.5A | 1A | 5.5A
Dimension (LxWxH) mm |  | 280x144x230 |  | 400x144x230 |  | 425x190x328 | 400x144x230
Weight |  | 7.8kg | 4.2kg | 13.3kg | 6.4kg | 23.4kg | 6.5kg
Working Temperature |  | 0℃-40℃
Working Humidity |  | 20%-95% (non-condensing)
Noise |  | ≤50dB

## Sheet2
Online High Frequency UPS (1/1 phase)
Parameter
Model |  | VT6KVA | VT6KS | VT10KVA | VT10KS
Rated Power |  | 6kVA/5.4kW |  | 10kVA/9kW
Input | Voltage Range | 120-275Vac 1P2W+G
| Working Frequency Range | 40-70Hz (settable)
| Input Power Factor | ≥0.99
Output | Rated Voltage and Accuracy | 220Vac(1±1%) 1P2W+G
| Output Frequency | 50Hz
| Rated Current | 27A |  | 45A
| Output Power Factor | 0.9
| Output Harmonic Wave | ≤3% (Full R load)
| Crest Factor |  | 3:01
| Output Overload | 105%±5%＜Load≤125%±5%: Convert to bypass output and alarm after 1 min;
125%±5%＜Load≤135%±5%: Convert to bypass output and alarm after 30s;
Load＞135%±5%: Convert to bypass output and alarm after 300ms.
Conversion time between Mains Power and Battery |  | 0ms
Efficiency |  | ＞92%
Battery | Rated Voltage | 192Vdc
| Quantity | 16
| Charging Current | 1A | 5.5A | 1A | 5.5A
Dimension (LxWxH) mm |  | 533x260x560 | 425x190x328 | 533x260x560 | 533x260x501
Weight |  | 55kg | 12.2kg | 62kg | 21kg
Working Temperature |  | 0℃-40℃
Working Humidity |  | 20%-95% (non-condensing)
Noise |  | ≤55dB

## Sheet3
Online High Frequency UPS (1/1 phase)
Parameter
Model |  | VT15KS | VT20KS
Rated Power |  | 15kVA/13.5kW | 20kVA/18kW
Input | Voltage Range | 120-275Vac 1P2W+G
| Working Frequency Range | 40-70Hz (settable)
| Input Power Factor | ≥0.95
Output | Rated Voltage and Accuracy | 220Vac(1±1%) 1P2W+G
| Output Frequency | 50Hz
| Rated Current | 68A | 91A
| Output Power Factor | 0.9
| Output Harmonic Wave | ≤3% (Full R load)
| Crest Factor | 3: | 1
| Output Overload | 105%±5%＜Load≤125%±5%: Convert to bypass output and alarm after 1min;
125%±5%＜Load≤135%±5%: Convert to bypass output and alarm after 30s;
Load＞135%±5%: Convert to bypass output and alarm after 300ms.
Conversion time between Mains Power and Battery |  | 0ms
Efficiency |  | ＞92%
Battery | Rated Voltage | 192Vdc
| Quantity | 16
| Charging Current | 5.5A
Dimension (LxWxH) mm |  | 533x260x501
Weight |  | 32kg | 33kg
Working Temperature |  | 0℃-40℃
Working Humidity |  | 20%-95% (non-condensing)
Noise |  | ≤60dB

## Sheet4
Online High Frequency UPS (3/3 phase)
Parameter
Model |  | VT33 10KS | VT33 20KS | VT33 30KS | VT33 40KS
Rated Power |  | 10kVA/9kW | 20kVA/18kW | 30kVA/27kW | 40kVA/36kW
Input | Voltage Range | 207-475Vac 3P4W+G
| Working Frequency Range | 40-70Hz (settable)
| Input Power Factor | ≥0.99
Output | Rated Voltage and Accuracy | 380Vac(1±1%) 3P4W+G
| Output Frequency | 50Hz
| Rated Current | 15A | 30A | 45A | 61A
| Output Power Factor | 0.9
| Output Harmonic Wave | ≤3% (Full R load)
| Crest Factor |  | 3:
| Output Overload | 105%±5%＜Load≤125%±5%: Convert to bypass output and alarm after 1min;
125%±5%＜Load≤150%±5%: Convert to bypass output and alarm after 30s;
Load＞150%±5%: Convert to bypass output and alarm after 300ms.
Conversion time between Mains Power and Battery |  | 0ms
Efficiency |  | ＞92% |  | ＞91%
Battery | Rated Voltage | 192Vdc |  | ±192Vdc
| Quantity | 16 |  | 32
| Charging Current | 1A | 1A | 5.5A
Dimension (LxWxH) mm |  | 560x260x717 | 710x260x717 | 710x260x717
Weight |  | 72kg | 98kg | 58.5kg | 62kg
Working Temperature |  | 0℃-40℃
Working Humidity |  | 20%-95% (non-condensing)
Noise |  | ≤60dB